Typical Specification

IWH-SPEC-01

Typical Specification for Lochinvar® Regent Tankless Water Heater

Models 500,000 – 1,000,000 Btu/Hr

The WATER HEATER shall be a LOCHINVAR Regent Model IWH________________(N,L) having a modulating input rating of _______________ Btu/Hr, a recovery capacity of _____________ gallons per hour (________gallons per minute) at a 100oF rise and shall be operated on (Natural Gas) or (LP Gas). The WATER HEATER shall be capable of full modulation firing down to 40 MBH with a turn down ratio of 12.5:1 (IWH0500), 18.75:1 (IWH07500) or 25:1 (IWH1000), and no required minimum flow.

The IWH0500 to IWH1000 WATER HEATER shall bear the ASME “HLW” stamp and all models shall be National Board listed.  The WATER HEATER shall be constructed with a single stainless steel water tube heat exchanger.  There shall be no banding material, bolts, gaskets or "O" rings in the header configuration.  The stainless-steel combustion chamber shall be designed to drain condensation to the bottom of the heat exchanger assembly. A provided trap shall allow condensation to drain from the heat exchanger assembly. The complete heat exchanger assembly shall carry a ten (10) year limited warranty (see warranty for details).

The IWH0500 to IWH1000 WATER HEATER shall be ANSI Z21.10.3 certified and listed by C.S.A. International under the latest edition of the harmonized test standards for the US and Canada. The WATER HEATER shall comply with the energy efficiency requirements of the latest edition of the ASHRAE 90.1 Standard.  The WATER HEATER shall be AHRI certified to meet 96% thermal efficiency (IWH0500) or 97% thermal efficiency (IWH0750-1000). The WATER HEATER shall be certified for indoor installation and special kits are available for outdoor installation.

The WATER HEATER shall be constructed with a heavy gauge steel jacket assembly, primed and pre-painted on both sides.  The combustion chamber shall be sealed and completely enclosed, independent of the outer jacket assembly, so that integrity of the outer jacket does not affect a proper seal.  A burner/flame observation port shall be provided.  The burner shall be a premix design and constructed of high temperature stainless steel to provide modulating firing rates. The WATER HEATER shall be supplied with a gas valve and regulator equipped with a proof of closure (POC) and a variable speed blower system, to precisely control the fuel/air mixture delivering modulating firing rates for maximum efficiency. The WATER HEATER shall operate in a safe condition at the rated output with gas supply pressures as low as 2.5 inches of water column for natural gas and 8 inches of water column for LP gas.

The WATER HEATER shall be equipped with a combustion control featuring RealTime O2 Trim™. This technology shall adjust the fuel/air ratio via 3 independent methods (air damper, gas damper, and fan speed). To achieve the optimal O2 the system shall utilize feed forward information (air temperature, barometric pressure), Commissioned trim (initial settings at commissioning), Learned trim (optimal settings learned during operation), and Feedback information (wet O2 value). The O2 sensor shall be located in the combustion chamber. The adjustments shall be in real time during operation, continuous throughout the entire modulation range, and be displayed via a gauge on the water heater touchscreen. No extra or 3rd party controller shall be required to commission the water heater or read O2 values.

The WATER HEATER shall utilize a 24 VAC control circuit and components.   The control system shall have an electronic display for water heater set-up, water heater status, and water heater diagnostics. All components shall be easily accessed and serviceable from the front and left side of the cabinet. The WATER HEATER shall be equipped with a high limit temperature control, ASME certified pressure relief valve set for 150 PSI, outlet water temperature sensor, inlet water temperature sensor, a flue temperature sensor, and low water flow protection. The manufacturer shall verify proper operation of the burner, all controls and the heat exchanger by connection to water and venting for a factory fire test prior to shipping.

A CIRCULATING PUMP is included to deliver specified flow rates through the heat exchanger.

The WATER HEATER shall feature the “SMART TOUCH” control with a Multi-Colored Graphic LCD touch screen display, password security, and USB PC port connection.  The WATER HEATER shall be capable of controlling a building recirculation pump utilizing a relay when unit is powered on. The WATER HEATER shall have the capability to accept a 0-10 VDC input connection for BMS control of setpoint and enable/disable of the water heater, and a 0-10VDC output of water heater modulation rate. The WATER HEATER shall have a built-in cascading sequencer.

The WATER HEATER should be capable of rotation while maintaining modulation of up to eight water heaters without utilization of an external controller.  Supply voltage for the IWH0500 to IWH1000 WATER HEATER shall be 120 volt / 60 hertz / single phase.

The WATER HEATER shall be equipped with a single terminal block assembly for high voltage electrical connection.  A low voltage connection board with data points for safety and operating controls, i.e., Auxiliary Relay, Auxiliary Proving Switch, Alarm Contacts, Runtime Contacts, Manual Reset Low Water Cutoff, Flow Switch, Building Management System Signal, Modbus Control Contacts and Cascade Control Circuit.

The WATER HEATER shall be installed and vented with a (select one):

(a) Direct Vent Sidewall system with a horizontal sidewall termination of both the vent and combustion air.  The flue shall be PVC, CPVC, Polypropylene or Stainless-Steel sealed vent material terminating at the sidewall with the manufacturers specified vent termination.  A separate pipe shall supply combustion air directly to the WATER HEATER from the outside.  The air inlet pipe may be PVC, CPVC, ABS, Galvanized, dryer vent, Polypropylene or Stainless-Steel sealed pipe.  The air inlet must terminate on the same sidewall with the manufacturer’s specified air inlet cap. The WATER HEATER’s total combined air intake length shall not exceed values listed in TABLE 1.  The WATER HEATER’s total combined exhaust venting length shall not exceed values listed in TABLE 1.  Foam Core pipe is not an approved material for exhaust piping.

(b) Direct Vent Vertical system with a vertical roof top termination of both the vent and combustion air.  The flue shall be PVC, CPVC, Polypropylene or Stainless-Steel sealed vent material terminating at the roof top with the manufacturers specified vent termination.  A separate pipe shall supply combustion air directly to the WATER HEATER from the outside.  The air inlet pipe may be PVC, CPVC, ABS, Galvanized, dryer vent, Polypropylene or Stainless-Steel sealed pipe.  The air inlet must terminate on the roof top with the manufacturer’s specified air inlet cap. The WATER HEATER’s total combined air intake length shall not exceed values listed in TABLE 1.  The WATER HEATER’s total combined exhaust venting length shall not exceed values listed in TABLE 1.  Foam Core pipe is not an approved material for exhaust piping.

(c) Sidewall Vent with Room Air system with a horizontal sidewall termination of the vent with the combustion air drawn from the interior of the building. The flue shall be PVC, CPVC, Polypropylene or Stainless-Steel sealed vent material terminating at the sidewall with the manufacturers specified vent termination. The WATER HEATER’s total combined exhaust venting length shall not exceed values listed in TABLE 1.  Foam Core pipe is not an approved material for exhaust piping.

(d) Vertical Vent with Room Air system with a vertical rooftop termination of the vent with the combustion air drawn from the interior of the building. The flue shall be PVC, CPVC, Polypropylene or Stainless-Steel sealed vent material terminating at the rooftop with the manufacturers specified vent termination.  The WATER HEATER’s total combined exhaust venting length shall not exceed values listed in TABLE 1.  Foam Core pipe is not an approved material for exhaust piping.

(e) Vertical Vent with Sidewall Air system with a vertical rooftop termination of the vent with the combustion air being drawn horizontally from a sidewall. The flue shall be PVC, CPVC, Polypropylene or Stainless-Steel sealed vent material terminating at the roof top with the manufacturers specified vent termination. A separate pipe shall supply combustion air directly to the Water Heater from the outside. The air inlet may be PVC, CPVC, ABS, Galvanized, Dryer Vent, Polypropylene or Stainless-Steel sealed pipe. The air inlet must terminate on a sidewall using the manufacturers specified air inlet cap. The WATER HEATER’s total combined air intake length shall not exceed values listed in TABLE 1.  The WATER HEATER’s total combined exhaust venting length shall not exceed values listed in TABLE 1.  Foam Core pipe is not an approved material for exhaust piping.

Table 1 Direct Vent Minimum/Maximum Allowable Air/Vent Lengths

Maximum unit dimensions shall be: Length ________inches, Width ________inches and Height __________ inches.  Maximum unit weight shall be_________pounds.

03/2026– Printed in U.S.A.