Typical Specification

AHP-SPEC-03

Typical Specification for VERITUS® Air Source Heat Pump Water Heater

Models 60,000 – 350,000 Heating Capacity Btu/Hr

The HEAT PUMP shall be a LOCHINVAR Model AHP _________having an output rating of _________ Btu/Hr. HEAT PUMP shall be capable of following performance at 80.6F ambient, 63% relative humidity, inlet water temperature of 70F and outlet water temperature of 120F.  Testing parameters are in the AHRI 1300 standard.  COP testing not done to a standard testing procedure shall not be accepted.

| Model | Maximum Output (Btu/Hr) | COP |
| --- | --- | --- |
| AHP060 | 66,688 | 4.61 |
| AHP140 | 136,381 | 4.27 |
| AHP200 | 203,069 | 4.38 |
| AHP280 | 272,762 | 4.27 |
| AHP350 | 339,450 | 4.34 |

Maximum unit dimensions shall be: Length ________inches, Width ________inches and Height __________ inches.  Maximum operating (wet) unit weight shall be _________pounds.

The HEAT PUMP shall have a scroll compressor with additional control for monitoring operation of compressor.  Control shall provide diagnosis of the compressor with indication lights for status and codes.  HEAT PUMP shall be factory charged with R513A refrigerant, ECM variable speed circulator pump, and double wall stainless steel condenser for potable water applications.  The complete heat pump assembly shall carry a one (1) year limited warranty.  Optional 5-year compressor warranty shall be offered by manufacturer.

The HEAT PUMP shall adjust the Evaporator fan speed depending on ambient temperature to optimize the performance of the heat pump.

The HEAT PUMP refrigerant circuit shall contain an electronic expansion valve, receiver, accumulator, filter drier and service ports for refrigerant gauges.

The HEAT PUMP shall be certified and listed by UL to UL 60335-2-40 standard.  The HEAT PUMP shall be certified for indoor and/or outdoor installation.

The HEAT PUMP shall be constructed with a heavy gauge sheet metal assembly and painted on both sides.  Manufacturer shall provide results of a 9,000-hour salt spray test.

The HEAT PUMP shall utilize a 24 VAC control circuit and components.   The control panel shall have a touch screen display for HEAT PUMP set-up, HEAT PUMP status, and HEAT PUMP diagnostics. All components shall be easily accessed and serviceable.  Control panel shall be remote mountable, inside or outside installation is acceptable.

The HEAT PUMP shall be equipped with low and high refrigerant pressure switches; short cycle control; outlet water temperature sensor and return water temperature sensor.

The HEAT PUMP control shall provide for “Cascade” to sequence and rotate while maintaining operation of up to sixty-four HEAT PUMPs. The HEAT PUMP shall be capable of controlling a valve and ECM variable speed pump that maintains constant delivery temperature to the storage tank. The HEAT PUMP shall have an optional gateway device which will allow integration with BACnet.  MODBUS TCP shall be standard feature.

The HEAT PUMP shall be equipped with terminal strips for electrical connection.  A high voltage terminal strip shall be provided for Supply voltage.  Supply voltage shall be 440-480V/3PH/60Hz or 208V/3PH/60Hz.

The HEAT PUMP Control Panel shall contain the low voltage connections for the outdoor sensor, system sensor, Alarm Contacts, Runtime Contacts, Back Up Enable contacts and Booster Fan contacts.

STANDARD CONSTRUCTION

The HEAT PUMP shall be constructed in accordance with the code requirements as standard equipment.

07/25 – Printed in U.S.A.