Typical Specification

KBX-O-SPEC-01

Typical Specification for Lochinvar® OUTDOOR KNIGHT XL™

Models 399,999 –999,000 Btu/Hr

The BOILER shall be a LOCHINVAR OUTDOOR KNIGHT XL Model KBX_________(N,L)-O having a modulating input rating of _________ Btu/Hr, an output of _________ Btu/Hr and shall be operated on (Natural Gas) (L.P. Gas).   The BOILER shall be capable of following performance:

| Model | Turndown | Minimum Input | Maximum Input |
| --- | --- | --- | --- |
| KBX0400(N,L)-O | 10:1 | 39,000 | 399,000 |
| KBX0500(N,L)-O | 10:1 | 50,000 | 500,000 |
| KBX0650(N,L)-O | 10:1 | 65,000 | 650,000 |
| KBX0800(N,L)-O | 10:1 | 80,000 | 800,000 |
| KBX1000(N,L)-O | 10:1 | 99,000 | 999,000 |

Maximum unit dimensions shall be: 50 inches Length, 24 inches Width and 45 inches Height.  Maximum operating (wet) unit weight shall be no more than 580 pounds.

The BOILER shall bear the ASME "H" stamp for 160 psi working pressure and shall be National Board listed.  The BOILER shall have a fully welded, stainless steel, water tube heat exchanger.  Multiple pressure vessels in a single enclosure are not acceptable. There shall be no banding material, bolts, gaskets or "O" rings in the pressure vessel construction.  The heat exchanger shall be designed for a single-pass water flow to limit the water side pressure drop.  Pressure drop shall be no greater than 2.2 psi at 75 GPM.  The condensate collection basin shall be constructed of welded stainless steel. The complete heat exchanger assembly shall carry a ten (10) year limited warranty.

The heat exchanger shall have a volume of water no less than:

| Model | Water Content |
| --- | --- |
| KBX0400(N,L)-O | 4.4 gallons |
| KBX0500(N,L)-O | 4.9 gallons |
| KBX0650(N,L)-O | 6.2 gallons |
| KBX0800(N,L)-O | 7.3 gallons |
| KBX1000(N,L)-O | 8.8 gallons |

The BOILER shall be certified and listed by C.S.A. International under the latest edition of the harmonized ANSI Z21.13 test standard for the U.S. and Canada.  The BOILER shall be certified for outdoor installation with ambient temperatures above 32°F.  The BOILER shall comply with the energy efficiency requirements of the latest edition of ASHRAE 90.1 and the minimum efficiency requirements of the latest edition of the AHRI BTS-2000 Standard as defined by the Department of  Energy in 10 CFR Part 431.  The BOILER shall operate at a minimum of 96.3% Combustion and Thermal Efficiency at full fire as registered with AHRI.  The BOILER shall also be certified for indoor installation.

The BOILER shall be constructed with a heavy gauge steel jacket assembly, primed and pre-painted on both sides.  The jacket shall be designed and sealed for outdoor installations.  The combustion chamber shall be sealed and completely enclosed, independent of the outer jacket assembly.  A burner/flame observation port shall be provided for observing the burner flame and combustion chamber.  The burner shall be a premix design constructed of high temperature stainless steel with a woven Fecralloy outer covering to provide smooth operation at all modulating firing rates. The BOILER shall be supplied with a negative pressure regulation gas valve and be equipped with a pulse width modulation blower system to precisely control the fuel/air mixture to the burner. The BOILER shall operate in a safe condition with gas supply pressures as low as 4 inches of water column.  The burner flame shall be ignited by direct spark ignition with flame monitoring via a flame sensor.

The BOILER shall utilize a 24 VAC control circuit and components.   The control system shall have a factory installed display for boiler set-up, boiler status, and boiler diagnostics. All components shall be easily accessed and serviceable from the front and top of the jacket. The BOILER shall be equipped with a temperature/pressure gauge; high limit temperature control with manual reset; ASME certified pressure relief valve set for 50 psi (standard); outlet water temperature sensor with a dual thermistor to verify accuracy; system supply  water temperature sensor; outdoor air sensor, flue temperature sensor with dual thermistor to verify accuracy; low water cut off with manual reset, blocked drain switch and a condensate trap for the heat exchanger condensate drain.

The BOILER shall feature the “SMART TOUCH™” control with CON-X-US which is standard and factory installed with an 7” liquid crystal touch screen display, password security, outdoor air reset, pump delay with freeze protection, pump exercise, ramp delay featuring six steps, domestic hot water prioritization with limiting capabilities and PC port connection.  A secondary control that is field mounted outside or inside the appliance is not acceptable.  The BOILER shall have alarm contacts for any failure, runtime contacts and data logging of runtime at given modulation rates, ignition attempts and ignition failures.  The BOILER shall have a built-in “Cascade” to sequence and rotate while maintaining modulation of up to eight boilers of different Btu inputs without utilization of an external controller.  The internal “Cascade” function shall be capable of lead-lag, efficiency optimization, front-end loading, and rotation of lead boiler every 24 hours.  The control must include cascade redundancy to allow a member boiler to become the temporary leader if the original lead boiler shall loose communication with the members.  The BOILER shall be capable of controlling an isolation valve (valve shall be offered by manufacturer) during heating operation and rotation of open valves in standby operation for full flow applications. The control must be equipped with standard BACnet MSTP and Modbus communication protocol with a minimum 55 readable points.  The BOILER shall have an optional gateway device which will allow integration with LON or BACnet (IP) protocols.

The “SMART TOUCH™” control shall include CON-X-US communication platform that will allow remote access via a smart phone or Tablet.  This will allow the ability to monitor and manage multiple KNIGHT XL Boilers and send alerts via text or e-mail notifying of changes in system status.  A user shall have the ability to check system status or re-program any boiler function remotely.

The “SMART TOUCH™” control shall increase fan speed to boost flame signal when a weak flame signal is detected during normal operation.  A 0 -10 VDC output signal shall control a variable speed boiler pump (pump to be offered by manufacturer) to keep a fixed delta t across the boiler regardless of the modulation rate.  The BOILER shall have the capability to receive a 0 – 10 VDC input signal from a variable speed system pump to anticipate changes in system heat load in order to prevent flow related issues and erratic temperature cycling.

The BOILER shall be equipped with two terminal strips for electrical connection.  A low voltage connection board with 44 connection points for safety and operating controls, i.e., Alarm Contacts, Runtime Contacts, Louver Proving Switch, Tank Thermostat, Domestic Hot Water Building Recirculation Pump Contacts, Domestic Hot Water Building Recirculation Temperature Sensor Contacts, Remote Enable/Disable, System Supply Temperature Sensor, Outdoor Temperature Sensor, Tank Temperature Sensor, Modbus Building Management System Signal and Cascade Control Circuit.  A high voltage terminal strip shall be provided for Supply voltage.   Supply voltage shall be 120 volt / 60 hertz / single phase on all models. The high voltage terminal strip plus integral relays are provided for independent pump control of the System pump, the Boiler pump and the Domestic Hot Water pump.

The BOILER shall have an independent laboratory rating for Oxides of Nitrogen (NOx) to meet the requirements of South Coast Air Quality Management District in Southern California and the requirements of Texas Commission on Environmental Quality.  The manufacturer shall verify proper operation of the burner, all controls and the integrity of the heat exchanger by connection to water and venting for a factory fire test prior to shipping.

The BOILER shall be suitable for use with polypropylene glycol up to a 50% concentration.  The de-rate associated with the glycol will vary per glycol manufacturer.

STANDARD CONSTRUCTION

The BOILER shall be constructed in accordance with the following code requirements as standard equipment.  Manufacturing of special models to meet the below code requirements is not acceptable.

California Code

Massachusetts Code

Kentucky Code

CRN Approval in Canada

Note:  Due to the large disparity in CSD-1 interpretation from state to state, please confirm to the factory all controls required in your jurisdiction.

01/21 – Printed in U.S.A.